Summary of Survey Result

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Testing Company | | | Survey Result Summary | | | | 안성시 일죽면 방초리 물류창고 | |
| Allen Face Korea | | | 2024-03-06 | | | | 1F | |
| ` | | | | | | | | |
| **Survey result** | | | | | | **Permitted Limit TR34 3rd Edition FM2** | | **Remark (TR34 3rd FM2)** |
| **SLAB ID** | **SLAB AREA** | **Measured** | **Measured** | **TR34 3rd Edition** | **TR34 3rd Edition** | **Property II** | **Property IV** | **PASS / FAIL** |
| **M2** | **OAFF** | **OAFL** | **Measure (95%)** | **Measure (100%)** | **FM2(FF 22.0)** | **FM2(FL 26.0)** |
| #1 | **NOP** | **32.7** | **38.5** | **FM2(Spectial)** | **FM2(Spectial)** | **FM2(FF 22.0)** | **FM2(FL 26.0)** | **PASS** |
| #2 | **NOP** | **29.7** | **23.3** | **FM2** | **FM2** | **FM2(FF 22.0)** | **FM2(FL 26.0)** | **PASS** |
| #3 | **NOP** | **44.9** | **38.9** | **FM2** | **FM2(Special)** | **FM2(FF 22.0)** | **FM2(FL 26.0)** | **PASS** |
| #4 | **NOP** | **30.0** | **30.2** | **FM2** | **FM2** | **FM2(FF 22.0)** | **FM2(FL 26.0)** | **PASS** |
| #5 | **NOP** | **41.3** | **30.7** | **FM2** | **FM2** | **FM2(FF 22.0)** | **FM2(FL 26.0)** | **PASS** |
| #6 | **NOP** | **30.3** | **29.0** | **FM2** | **FM2** | **FM2(FF 22.0)** | **FM2(FL 26.0)** | **PASS** |
| #7 | **NOP** | **32.3** | **25.5** | **FM2** | **FM2** | **FM2(FF 22.0)** | **FM2(FL 26.0)** | **PASS** |
| #8 | **NOP** | **34.8** | **42.0** | **FM2** | **FM2** | **FM2(FF 22.1)** | **FM2(FL 26.1)** | **PASS** |
| #9 | **NOP** | **31.1** | **28.9** | **FM2** | **FM2** | **FM2(FF 22.2)** | **FM2(FL 26.2)** | **PASS** |
| #10 | **NOP** | **35.2** | **29.2** | **FM2** | **FM2** | **FM2(FF 22.3)** | **FM2(FL 26.3)** | **PASS** |
| #11 | **NOP** | **46.7** | **33.1** | **FM2** | **FM2** | **FM2(FF 22.4)** | **FM2(FL 26.4)** | **PASS** |
| #12 | **NOP** | **34.5** | **21.2** | **FM2** | **FM2** | **FM2(FF 22.5)** | **FM2(FL 26.5)** | **PASS** |
| #13 | **NOP** | **28.8** | **27.9** | **FM2** | **FM2** | **FM2(FF 22.6)** | **FM2(FL 26.6)** | **PASS** |
| #14 | **NOP** | **30.9** | **35.6** | **FM2** | **FM2** | **FM2(FF 22.7)** | **FM2(FL 26.7)** | **PASS** |
| #15 | **NOP** | **52.0** | **39.3** | **FM2** | **FM2** | **FM2(FF 22.8)** | **FM2(FL 26.8)** | **PASS** |
| Average |  | **35.7** | **31.6** |  |  | **Permitted Limit TR34 3rd Edition FM2** | | **PASS** |

`